## PPM Schedule
ESYBOXmini3 / ESYBOX
Planned Preventive Maintenance schedule
Equipment / Activity | Frequency | [52 empty] | LEGEND | time axis 2024-01-01 to 2024-12-23
Cold Water Booster | Week | [52 empty] | D | Daily | time axis 2024-01-01 to 2024-12-23
Check For Alarms / RED alarm LED on the screen | D | [52 empty] | W | Weekly
Flush Pump back to tank and check for debris | W | [52 empty] | M | Monthly
Check flow reading while running irrigation cycle | W | [52 empty] | 3M | 3 Monthly
Check power PO Power output reading during running cycle | W | [52 empty] | T | Termly
Log/Record flow Meter Readings | W | [52 empty] | 6M | 6 Monthly
Flush through and purgeLittle used outlets | W | [52 empty] | Y | Yearly
Inspect storage tank for debris / scale build-up | M | bar: 2024-01-29; 2024-02-26; 2024-03-25; 2024-04-22; 2024-05-20; 2024-06-17; 2024-07-15; 2024-08-12; 2024-09-09; 2024-10-07; 2024-11-04; 2024-12-02
Inspect check valve and clean / replace as necessary | M | bar: 2024-01-29; 2024-02-26; 2024-03-25; 2024-04-22; 2024-05-20; 2024-06-17; 2024-07-15; 2024-08-12; 2024-09-09; 2024-10-07; 2024-11-04; 2024-12-02
Inspect self priming valve, clean / replace as necessary | 3M | bar: 2024-04-01; 2024-07-01; 2024-10-07
Check the power leads for damage | 3M | bar: 2024-04-01; 2024-07-01; 2024-10-07
Check system for leaks | 3M | bar: 2024-04-01; 2024-07-01; 2024-10-07
Flush with Hydrogen Peroxide - Diluted to ~34% & reflush with clean water | 6M | bar: 2024-07-01
Clean storage tank | 6M | bar: 2024-07-01
Check Fault History log faults and reset if necessary | 6M | bar: 2024-07-01
Check the recepticals the pumps are pluged into | Y
Check Pre Charge air Pressure with pump off and water pressure released | Y

## How too Guide
Back too PPM Schedule
Check flow reading while running irrigation cycle
1) Press the Set Button to wake the screen up and move back to the main screen
2) Press the MODE button once to move to the user info screen with the VF flow reading
3) log the VF flow reading while running the cycle
4) Compare the previous readings to check for potential differences which could show potential future issues
Check power PO Power output reading during running cycle
1) Press the Set Button to wake the screen up and move back to the main screen
2) Press the MODE button once to move to the user info screen with the VF flow reading
3) log the PO Power Output reading while running the cycle
4) Compare the previous readings to check for potential differences which could show potential future issues
Log/Record flow Meter Readings
1) Press the Set Button to wake the screen up and move back to the main screen
2) Press the MODE button about 4 times to move to the user info screen with the total & partical flow readings
3) log the Total Flow readings
4) Compare the previous readings to check for potential differences which could mean incorrect watering volumes
| ESYBOX mini3 |  | ESYBOX
Inspect check valve and clean / replace as necessary
1) power down or unplug the pump
2) release the water pressure from the system by opening a valve on the discharge
3) unscrew the check valve cover
4) inspect the inbuilt check valve, clean and replace if necessary
5) refilt the inbuilt check valve
5) reprime the pump and check the operation of the pump and that it holds pressure when no water is being used
Inspect self priming valve, clean / replace as necessary | ESYBOX mini3 | ESYBOX
1) power down or unplug the pump
2) release the water pressure from the system by opening a valve on the discharge
3) unscrew the self priming valve cover
4) inspect the self priming shutter valve & spring, clean and replace if necessary
5) refilt the self priming shutter valve
5) reprime the pump and check the operation of the pump and that it holds pressure when no water is being used
Check Fault History log faults and reset if necessary
1) Press the Set Button to wake the screen up and move back to the main screen
2) Press the MODE button about 7 times to move to the FF faults and warning screen
3) log the the Faults if there are any
4) Reset if you want
| ESYBOX mini3 | ESYBOX
Check Pre Charge air Pressure with pump off and water pressure released
1) power down or unplug the pump
2) release the water pressure from the system by opening a valve on the discharge
3) unscrew valve cover
4) check the precharge with a trie presure gauge
5) adjust the pressure to 14 psi below the SP set pressure
6) refit the valve cover
7) reprime the pump and check the operation of the pump and that it holds pressure when no water is being used